CYCWJ-406型温度测量模块使用说明书

CYCWJ-406型温度测量模块专门用于多点温度变换，配合上位机使用，广泛适用于仓库、化工、医药、保鲜等行业。

一、主要特点：

1、防水、防潮，体积小，接线端子内置，运行可靠，安装简便。

2、端口驱动能力强，可接入1-6个数字化温度探头，精度高，无须校准。

3、具有光电隔离的RS485通讯接口，抗干扰能力强。

4、全部采用可插拔接插件，便于维修、更换。

二、面板说明：

1、指示灯 RUN：运行指示，正常运行时间歇闪烁。

2、指示灯 COMM：通信指示，通信成功，闪烁1次。

3、指示灯 FLAG：故障指示。

三、接线说明：

- 拧开上盖上的6个螺丝，打开上盖。如图所示：

2、有两组温度探头接入，1组接T1、T2、T3；2组接T4、T5、T6。当探头数不足6个时，必须按顺序接入。

3、以1组为例：探头的红线为正极，3个探头的红线并在一起接5V；探头的黑（黄）线为地线，3个探头的地线并在一起接GND；探头的绿（蓝）线为信号线，分别接T1、T2、T3。 接好探头线后插到座上，2组同样。

4、网线的绿白线接+A；绿线接-B；棕线和棕白线并在一起接通信口的GND。

5、电源接口为220V交流电，接入时要确保接的可靠，线头不要过长，以免碰到别处，造成危险。

四、模块号、探头数、运行模式设定：

1、运行模式设定：SENS拨码开关（红色的）的1号开关拨到on，出厂已作设定，用户不需改动。

2、模块号设定：ADDR拨码开关。在一个系统中，每个模块的地址必须是唯一的，不能重复。设置方式请参照机号表格

| 机号 | 1 | 2 | 3 | 4 | 5 |
| --- | --- | --- | --- | --- | --- |
| 1 | on | off | off | off | off |
| 2 | off | on | off | off | off |
| 3 | on | on | off | off | off |
| 4 | off | off | on | off | off |
| 5 | on | off | on | off | off |
| 6 | off | on | on | off | off |
| 7 | on | on | on | off | off |
| 8 | off | off | off | on | off |
| 9 | on | off | off | on | off |
| 10 | off | on | off | on | off |
| 11 | on | on | off | on | off |
| 12 | off | off | on | on | off |
| 13 | on | off | on | on | off |
| 14 | off | on | on | on | off |
| 15 | on | on | on | on | off |

3、探头数设定：SENS拨码开关。按照接入的探头数设定，参照探头数设定表格。

| 探头数 | 1 | 2 | 3 | 4 |
| --- | --- | --- | --- | --- |
| 1 | On | On | Off | Off |
| 2 | On | Off | On | Off |
| 3 | On | On | On | Off |
| 4 | On | Off | Off | On |
| 5 | On | On | Off | On |
| 6 | On | off | On | On |